## Sheet1
TDKA 24-2510, Renovate Hanger 140
RFI Responses as of 15 October 2024
# | Contractor Questions | Government Answers
1 | It is mentioned on various Drawings that many areas of construction are very congested & may not provide adequate room for installation of MEP elements/equipment. Any pictures or details of these areas. | All asbuilt documents available for facility have been provided with RFI responses. Contractor site walk (conducted 18 SEP) is intended to get eyes on these various conditions.
2 | What is gap/ space available in between Drop ceiling to provide air distribution and electrical components. | All asbuilt documents available for facility have been provided with RFI responses.
3 | No Drawings is available in the documents showing locations/details of sprinkler head/system. SOW is asking to provide new sprinkler heads for proper fit in ceiling, any drawings or respective information to quantify this work. | As-builts and Contractor site visit should provide adequate information to quantify this work along with room sizes presented in the drawings.
4 | Which are the critical areas where contractor need to provide temporary heat/cool during demo and installation of new system. | Contractor shall ensure no damage to the building due to lack of heating and ensure that occupied spaces are of adequate temperature per UFC for office work. Hanger heating system shall be left functional throughout. See response to #117 for information on occupied areas.
5 | Can we get existing system as builds to verify quantities of Demolition at MEP works. | All asbuilt documents available for facility have been provided with RFI responses.
6 | SOW 2.6.2 request to reuse existing piping system to the point of not being able to use, however drawings are requesting all new chilled water piping to be NE, please clarify up to, what extent we can use the existing piping. | In accordance with SOW 2.6.2 contractor shall take into account prior to bidding the worst case scenario and plan to replace piping back to a reusable point. No known chilled water piping in the facility. Existing hot water piping may be reused where in good condition. Please identify any chilled water piping that you would like to reuse if you have further questions.
7 | HV1 Trans as shown on EP-101A is this existing utility Transformer from where the contractor is to install mains feeder connecting mains panel in room 112A or it is HV1S please confirm | It is Transformer HV1S, see updated drawings on sheet EP-101A
8 | If the above is HV1S than what is the location of utility transformer | Per the two site visitis, the existing utility transformer is located outside just southeast of Entry Vest 110C
9 | What is the Switch board shown in Room 112A with out any designation, is this the New Main Switch Board MSB please confirm | It is confirmed as the new MSB
10 | Any information on existing Fire Alarm, Mass Notification, Intruder detection & access control systems. | Per the two site visits, it is a EST-3 Fire Alarm System. All available existing asbuilts have been provided with these RFI responses.
11 | Will the Government consider an extension of the proposal submission deadline, given that the current due date falls immediately after a holiday weekend? | The FOPR has been amended to have a new proposal deadline of 30 October 2024 at 10:00AM Mountain Time
12 | Could the Government kindly confirm the designated location or format where they would like offerors to acknowledge receipt of amendments? | In accordance with paragraph 5 of the FOPR. Each Offeror shall acknowledge receipt of any amendments in conjunction with the Offeror’s proposal. This can be done in the format of the offeror's choosing via the Cover Letter or email submission
13 | Can the Government please confirm whether they require only one Prior Experience Citation as part of the proposal submission? | Confirmed, the Government only requires one Prior Experience Citation meeting the criteria included within the FOPRto be considered acceptable.
14 | Will the Government kindly confirm whether there is a page limitation for Volume 1 of the proposal? | There is no page limitation for the Cover Letter required in Volume 1. Regarding the offerors technical response the Government requires offerors to submit the informaiton via Attachment 10 of the FOPR. If there is insufficient room on Attachment 10 then offerors may submit a supplementary attachment not to exceed 2 pages (Rev ised in FOPR Paragraph 7 - Technical Factors).
15 | Would the Government permit offerors to recreate the Attachment 10 Prior Experience Citation form? | The Government requests offerors to utilize the provided form. If there is insufficient room on Attachment 10 then offerors may submit a supplementary attachment not to exceed 2 pages (Rev ised in FOPR Paragraph 7 - Technical Factors).
16 | Could the Government please confirm the specific font size they require for the proposal submission? | No restriction on font size has been established or identified in the FOPR. However, the Government requests that font size be 10pt or larger
17 | The Access Control system panel will be housed in telecom room 106E? Please confirm. | Per SOW 2.12.2, IDS and ACS systems must comply with DoDM 5200.01 Vol 3, which dictates expected locations of PCU equipment (near entrances on the secure side). Note that sheet G002 indicates (3) separate secure boundaries that all require independent IDS/ACS reporting.
18 | In Conference room 105 there are six (6) data drops identified at the conference table, two NIPR and two SIPR. Question, what network are the remaining two supposed to be? | See drawings sheet IF-101 and associated legend for information regarding these drops.
19 | In the Shared SIPR Café (rm. 107) there are seven (7) TV outlets. Do these call for a SIPR CAT6 or another type of AV media? | The power and data feeds shown in this room are for systems furniture connection, not TVs. See "IF" series drawings for specific data drop designations at each systems furniture assembly. Note: Keynote 26.204 is not exclusive to TV outlets.
20 | In the SOW 2.10.8.4, it calls for a backbone cabling from TR to TR, 12 strands of 62.5/125 multimode and 24-strands of 9/125 single-mode cable within a single jacket. Does this include from TR 110A to TR 119? If so, what and where is the conveyance mode to be provided for this north to south side run? | The backbone cabling from TR110A to TR 119 is existing and sufficient. No additional NIPR backbone cabling needed from area A to area B
21 | For cost reduction, can the 12 strands of 62.5/125 multimode and 24-strands of 9/125 single-mode cable in question 20 above be two separate cables? | This is acceptable.
22 | Are the CAT6 cable terminations to be in T-568A or T-568B pinout? | T-568B
23 | On sheet EC-101C, there is room103, identified as “Print/Comm”; are there to be any Comm cable terminations within this room? | yes, there is one Comm drop in this room reflected on sheet EC-101. No, it is not a comm room.
24 | In Conference room 212 there are six (6) cable drops at the conference table, two NIPR and two SIPR. Question, what network are the remaining two supposed to be? | Also answered in #18. See drawings sheet IF-101 and associated legend for information regarding these drops.
25 | In room 212, what type of conveyance is to be provided for cable installation to this table? | See SOW 2.3.6.5 for requested information.
26 | On the conference tables, what type of termination box is to be used? Please describe the conveyance required from the floor and up through the table. | See SOW 2.13.16.1 for requested information. Note that comm and power cabling must be fed direct into the conference tables and systems furniture without patch cables or intermediate wall/floor box termination. (Per General Notes on IF-101 and IF-102)
27 | The Statement of Work in paragraph 2.9.5.1 states to provide a complete and functional lightning protection system for Building 140, compliant with UFC 3-575-01. Per the AFMAN 32-1065 A5.1.15 “Adhesive Fasteners for down conductors and cross conductors of an integral system are not allowed on Air Force Facilities due to the short life of the adhesive”. Per the UFC 3-575-01 3-2.1 for Air Force “If adhesive fasteners must be used, an inspector who is familiar with the installation of these adhesive fasteners must watch during the installation and verify in writing (print name after signature) in the test records for that facility / structure that the installation was in accordance with manufacturer’s instructions”. Can adhesive be utilized on this reroof project. Installation under the roofing membrane will be a phasing concern considering the roofing contractor is planning on tearing off and replacing sections each day. Additionally, installing conductor with adhesive fastened on top of the membrane will drastically reduce the number of roof penetrations and chances for a potential leak. | Mechanically attached conductors should be used to the greatest extent feasible at areas where can be mounted to side fascias, parapets, etc. without impacting the integrity of the roof assembly itself. Where attached to the roof surface, adhesive fasteners are acceptable, as long as UFC 3-575-01 is followed for compliance.
28 | The Design Guide in paragraph 8.12.9 states the preferred method of facility grounding is with a ground ring. AFI 32-1065, a ground counterpoise will be required if individual ground rods cannot achieve a grounding resistance test less than 25ohms. Will a ground loop be required? | A ground loop is not required. A triangular counterpoise of three ground rods at each corner is required.
29 | If a ground loop is required, does the loop need to be installed 3’-0” to 8’-0” away form the building foundation as required by AFMAN? | See response to question 28
30 | Per the Peterson SFB Design Guide paragraph 8.7.2 states ground rods shall be copper. Are copper -clad ground rods acceptable? Solid copper ground rods are not readily available. | Copper clad ground rods are acceptable
31 | What is the concrete thickness on the flightline around building 140? | KTR to assume a maximum thickness of 12"
32 | Will down conductors be allowed to be run exposed on the skin of the building to avoid unwanted penetrations in the roof? | Regardless of interior or exterior routing of utilities and down conductors, they are not permitted to be exposed/visible per PSFB Design Guide. Contractor is required to provide concealment matching the facility aesthetic adjacent. On this facility, this will need to match the material and color of the exterior metal panel system in most cases.
33 | Please provide finish paint color and product. | See revised sheet A-603 for finishes information, as well as PSFB Design Guide, section 5.7.14 for paint requirements.
34 | In Attachment 6, “Asbestos_Inventory_and_Testing_Reports_20240801”, in the summary table on page 2 it lists drywall throughout building as being tested and found to not contain asbestos. However, the reports in the same document have 3 drywall samples taken from the hanger area. These samples show the texture does not contain asbestos, but the joint compound does contain asbestos. For the purposes of bidding, should we assume that all drywall texture does not contain asbestos, and all joint compound does contain asbestos? | This noted joint compound sample was in an isolated area not being touched by this project. Bidders shall assume that all drywall texture AND all joint compound does not contain asbestos until otherwise indicated in further testing.
35 | In the SOW, it states, “2.3.1.2. Not all demo/relocation of existing utilities is indicated. Contractor shall be responsible to demo/relocate existing utilities as needed to accomplish all work. Any selective wall or gypsum board demolition required for utility installation/relocation shall be patched and refinished/textured prior to receiving new paint or other finish as indicated.” Without drawings showing the additional gypsum board demolition, how should we bid that removal if the material (i.e., the joint compound) is asbestos containing and not already in the scope of demolition? | It is the contractor's responsibility to coordinate extent and amount of work required above ceiling with the SOW, Asbuilts and drawings, and match ceiling demolition/replacement accordingly. Please take special note of SOW 2.2.3, 2.3.3.3 and Drawing sheet G002 for expectations on ACM lid demolition expectations and non-ACM gypsum lid demolition expectations.
36 | In the SOW, it states, “2.3.1.5. Not all required slab demolition is shown in the drawings. Where plumbing fixture rearrangements or piping/waste line rerouting must occur to comply with the drawings, Contractor is responsible for any sawcutting, trenching, and concrete slab infill necessary for coordination with new locations of slab penetrations.” Without drawings showing the additional slab demolition, how should we bid for the additional abatement necessary if there is asbestos containing flooring present that is not already scheduled for abatement? | It is the contractor's responsibility to coordinate extent and amount of work required for plumbing rework with the SOW, Asbuilts and drawings, and match slab demolition/infill accordingly. Please take special note of SOW 2.3.5.2 and Sheet A-603 for flooring replacement and demolition expectations.
37 | Will there be a plumbing, electrical and mechanical plan coming out and will you require the demo portion to be done by specific trades or would you like us to include it in our bid. | Existing facility asbuilts are provided with these RFI responses, no additional MEP demolition plans will be provided. See SOW for demolition scope. The second half of this question appears to be directed toward the prime contractor associated with the specific bid team. Not for Government Response.
38 | There is a lot of old, dead MEP between the gypsum board and tile ceiling. If the answer to the above question is to have each trade demo rather than us, would you at least like for us to demo this specifically as it generally is cheaper to have demolition remove what they can. | This question appears to be directed toward the prime contractor associated with the specific bid team. Not for Government response.
39 | How far back are we looking to remove the concrete pad for the new stairways. There is significant damage, and it would be helpful to know how much will need to go. There was an area with a hole in it that seemed to have a lot of empty space. There is clearly water erosion and it's unknown the extent of erosion underneath all of the concrete and how much empty space there is. We would need to further assess prior to bringing equipment on site and come up with a safety plan for the removal. | Existing concrete is to be removed as needed to provide a sound face for new concrete to be placed against and as required for execution of work outlined in the SOW and drawings. Assume that 10% of the fill below concrete has been lost to water erosion where new fill material is not already required by the SOW and Drawings.
40 | Are you looking to have us remove the ACT to the joist and if so, will this be done for both levels or just one and if just one which level would that be. | This question is unclear. If the intent is to request extents of Acoustical Ceiling Tile system demolition, this scope is captured on the AD-11X sheets in the drawings. If this is related to ACM lids or non-ACM lids, please see SOW 2.2.3, 2.3.3.3 and Drawing sheet G002 for expectations.
41 | The plans call for removal of insulation from the ceiling from the first floor. Can you confirm that is accurate as we didn't see any in the areas that we were able to look at. | Question is unclear. If this question is related to SOW 2.14.23.1.5, please re-review the roofing section, and the associated boundaries of Roof Type B on Sheet A-103 as well as roof assembly information on the same sheet. Roof B area is noted in asbuilts to have 2" existing attic insulation.
42 | Do you have any requirements in regard to dumpsters for this project. We normally include dumpsters in our bid though sometimes on the military projects the GC takes care of it due to logistics and security. | This question appears to be directed toward the prime contractor associated with the specific bid team. Not for Government response.
43 | SOW Paragraph 1.19. Is the scope of the fire protection design analysis the entire building or just the rooms/spaces on Drawing G002 labeled as Scope Area? | The fire protection design analysis must address the compliance metrics outlined in UFC 3-600-01, 1-7.2.2 for the scope of work areas part of this project. However, some of these metrics (means of egress, facility construction type, allowable area/height, vertical opening provisions, occupancy separations, etc) may extend beyond the sole boundary of the scope of work area to ensure compliance for the scope of work area itself. In other words, it is not the intent for the project to address compliance for spaces outside our boundaries, but information on those external spaces may be necessary to inform the analysis of the spaces within this project.
44 | Could the record drawings of the fire protection (sprinklers, fire alarm, and hanger foam system) be provided for review prior to the proposal due date? | See above. All available asbuilts for the facility are provided with these RFI responses.
45 | Could the record drawings of the site utility plans showing the building’s water service (domestic and fire) and the fire hydrants serving the building be provided prior to the proposal due date? | Utilities Map provided with RFI responses (Hydrants 211, 205, 206)
46 | Could the latest fire hydrant flow test of the closet fire hydrants be provided prior to the proposal date? | Hydrant flows provided with RFI responses
47 | Are there any known fire or life safety deficiencies for B140? | Yes, there are known FSDs. The FSDs relevant to the project and required to be corrected are incorporated into the SOW and drawings.
48 | Will Drawing G002 be provided with a summary of the maximum allowable quantities of hazardous materials stored prior to proposal date? | This question appears to be directed toward hazardous facility contents for NFPA 101 compliance. The Hazardous materials plan on G002 is intended to convey existing hazardous building materials requiring abatement, not hazard of contents associtated with NFPA 101. The Government is not aware of any hazardous contents of the facility of large enough quantity to trigger any mitigative construction/facility protection features. This hangar is an aircract storage/staging facility, not a maintenance facility. If the QFPE discovers or determines quantities of hazardous materials to be exceeding thresholds, this would need to be addressed in the Fire Protection Design Analysis.
49 | Can existing code study plans with existing fire walls, hazard protection, construction types, and egress summaries be provided prior to the proposal due date? | All available asbuilts are provided with these RFI responses. The Government has not found any existing life safety plans in the asbuilt documentation, and thus has produced the life safety plans on G101 and G102 from scratch IAW UFC and NFPA 101.
50 | Are any of the electronic equipment rooms or comm rooms following TSFPEWG G 3-600-01.01-18 for fire protection criteria in accordance with UFC 3-600-01 4-15.1.2? a) If so, can the mission assurance category rating required be provided prior to proposal date? b) If so, are contractors required to include any of the TSFPEWG construction requirements in their proposals (I.E.dedicated smoke exhaust/make up air, supervised fire protection zone with flow device, very early smoke detection, etc.) | All electronic equipment rooms must follow TSFPEWG G 3-600-01.01-18. a.) All electronic equipment in this project is listed as INCIDENTAL per TSFPEWG G 3-600-01.01-18. b.) Contractor must comply with TSFPEWG G 3-600-01.01-18 specifically para 1-5.1 that does not require any unique or additional features.
51 | Sheet AD101A shows the door between Rm. 130 & 135 with a demo hatch but does not include a keynote 8.01. Please clarify. | Per the demolition legend graphics, this door is to be demolished. Keynotes are a supplement to the graphic information.
52 | Detail 1, A-401 appears to have a 3 lavatory wide counter but does not show a Keynote for SP-04. Please confirm a full length mirror is required at this location. | See referenced elevation 4/A-401 (referenced in 1/A-401) for requested information.
53 | It appears Keynote 10.53 doesn't occur at all toilet partitions shown. Please confirm any location with toilet partitions shown are required to have new toilet partitions installed. | Per new plan graphics legend (ref A-101A through A-102B), new toilet partitions to be provided are appropriately represented with black/bold lines. As such, all toilet partitions in facility are noted to be replaced/new.
54 | SOW 2.1.4 requires secure boundary to comply with enclosure 3 of DoDM 5200.01 Vol. 3. a) Please confirm this secure boundary is not intended to be a vault IAW para. 1.A b) Is paragraph 1 "Vault and Secure Room Construction Standards" the intended section of compliance or are other sections of this document applicable? If so, please clarify which sections. | a) Confirmed. b) The secure areas in this project are required to comply with physical security standards, IDS, and ACS specifications for "secure rooms" within the Appendix to Enclosure 3.
55 | SOW 2.2.5 states "Additionally, contractor shall assume that there are other various ACM materials throughout facility not identified herein that will require testing and potential abatement...." It seems that this is indicating that contractors shall include the cost of this "unknown" abatement in their proposals. It is understood that testing of potentially ACM containing areas is to be included, but including the cost of the abatement will likely cause an artificial inflation of all contractors proposals. It appears that section 2.2.8 is stating that any asbestos not included within sections 2.2.3 or 2.2.4 will be a differing site condition. Please clarify. | It is not the intent of section 2.2.5 to expect bidders to include unknown material quantities in bid. The intent of this language is purely to caution the awarded contractor to the need for thorough investigation and testing of materials for proper safety. Section 2.2.8 explicitly references section 2.2.3, 2.2.4 and the Hazardous Materials plan to ensure that 2.2.5 is not interepreted as a bidding expectation for unknown materials.
56 | SOW 2.3.1.1 and following paragraphs appear to indicate demolition as required to accomplish all work with the exception of SOW 2.6.2 Mechanical and SOW 2.9.2 Electrical which appear to indicate full demolition of the systems. Please confirm the intent is only to demolish what is specifically required in the SOW, and all other items may remain. | It is not the intent of section 2.3.1.1 to supersede the MEP sections of the SOW. The statement "as indicated" is intended to point to other demolition references within the SOW as well as the drawings, and "as required" is intended to reference various materials demolition not explicitly called out but necessary for the scope of work identified (for example, demolition of duct insulation around a duct being demolished, or demolition of a section of gypsum ceiling to get new piping installed within the plenum). Both the MEP demolition requirements AND this section must be met.
57 | Please provide all available as-builts for Building 140. | All available asbuilts are provided with these RFI responses.
58 | SOW section 2.14.14 states "The contractor shall conduct hazardous material testing for the existing roof system. If hazardous materials exist proper mitigation measures must be taken during demolition. Contractor shall assume mitigation measures will be needed." It is unclear what this section is referencing. If asbestos is found during the testing, is the contractor to assume to mitigation/abatement of roofing materials should be included within our proposals? | Again, this section is not intended as an expectation for bidders to include unknown hazardous materials abatement costs within the bid, but rather as a caution to the awarded Contractor for safety and expectations upon discovery of such materials. No hazardous materials are known currently within the roofing system.
59 | SOW section 2.14.17 requires maintenance of air, moisture and vapor barriers. Please confirm there is no requirement for air, moisture or vapor barriers, other than maintaining the integrity of a system that already exists. | This question is unclear. The roofing system is specified as new. Continuity of air, moisture, and vapor control layers is an essential part of every building envelope and roofing system. The determination of where these layers each reside within the assembly changes from application to application, but must be maintained and not ignored. See also response to question #141.
60 | SOW 2.14.23.1.18 states to refer to UFC 3-110-03 for Snow Retention Device requirements. Stated UFC makes mention that designers should consider snow guards in ASHRAE climate zones 4 and above. It doesn't appear any of the design drawings have incorporated snow guards, but the SOW does. Please clarify if the designer (CE) requires snow retention. | Colorado Springs is in ASHRAE Climate Zone 5B, so snow retention devices are required. Follow UFC guidance on installation. Manufacturer selected may submit devices for approval for use and government will verify they meet in-service loads considering roof slope and design snow load.
61 | FOPR section 7b states "Offerers shall hold pricing valid through 31 October 2024". FOPR section 23 states "..Proposals shall be valid until 31 December 2024." Please clarify which is correct. | Pricing shall be held valid through 31 December 2024. FOPR has been revised to reflect this throughout.
62 | SOW 2.14.23.1.5 states "Existing thermal insulation in attic shall be replaced with new blanket insulation meeting a R-value of 49. There will be no additional insulation required above deck for SSMR." Detail 3 of A-103 details "New R-49 Blanket Thermal Insulation" on the New Standing Seam Metal Roof Assembly. Please clarify which is correct. | Question is unclear. These statements are not conflicting. Blanket insulation in attic is below roof deck, not above. See notes on A-103 indicating "Attic" space
63 | Detail 3 of A-103 appears to indicate new gypsum hard lid above acoustical ceiling. However, SOW and RCP sheets of the drawings only indicated demolition/abatement of these hard lids, not replacement. Please clarify if hard lids are to be re-constructed after abatement. | Bidder has answered this question already. The drawings/SOW are complementary. Per 3/A-103, new gypsum lid is required throughout areas receiving standing seam metal panel roofing, for containment/retention of the new R-49 blanket insulation within the attic space. For areas outside this Roof B scope of work, hardlids are only to be installed where shown on the RCPs as a finished ceiling surface.
64 | Drawing sheet A-401 indicates a Keynote 10.54 for new access panel, but this keynote cannot be found in the plan views. Does this occur on this sheet? | This keynote does indeed exist on this sheet. Please see keynote reference on detail 2/A-401 (plan East end of plumbing chase)
65 | Drawing sheet A-401 indicates an equipment note SP-01, but this keynote cannot be found in the plan views. Does this occur on this sheet? | SP-01 is only shown to be installed in Shared_Break Room 137.
66 | Drawing sheet A-402 indicates a Keynote 10.52 for new FEC, but this keynote cannot be found in the plan views. Does this occur on this sheet? | This keynote does indeed exist on this sheet. Please see keynote reference on detail 1/A402 outside TLT 102E.
67 | Drawings sheet A-410, detail 12 states "All exterior railings shall be hot dip galvanized. All interior railings shall be painted." SOW 2.3.7.4 states "All new metal stairs and railings shall be constructed of hot-dip galvanized steel." a) Are interior railings to be galvanized or painted? b) Are galvanized railings to receive a color topcoat or is the required finish galvanized? | See SOW revisions to 2.3.7.4 for clarification. All new exterior metal stairs and railings shall be constructed of hot-dip galvanized steel with a high performance coating matching the color of existing exterior (P-4), and all new interior metal stairs and railings shall be constructed of hot-dip galvanized steel with no additional coating.
68 | A-603 Finish Schedule indicates a "CG-1" wainscoting. Where does this occur? | A note has been added to the Finish Material Schedule. This is not wainscotting, but corner guards at all exterior corners.
69 | Will the government provide adequate power and water for the duration of the project? | This question is unclear. The contractor can use on-site water and electrical service for any construction operations.
70 | Is there any specific phasing for the asbestos removal? | No. This is up to the Contractor's means and methods, in conjunction with provisions of SOW 1.12
71 | Can we place waste receptacles inside of the hanger close to the work area? | See SOW 1.18
72 | Will temporary heating/cooling be a requirement at anytime during construction? | Repeat question. See item 4 above.
73 | SOW 2.6.3.1 Provide new grilles and diffusers with proper contractor provided airflows for the space…Is the contractor responsible for determining airflow rates for the building? | Airflow rates are provided in the drawings for the basis of design equipment; if/when the contractor uses a different piece of equipment they will have to update airflows as approved.
74 | SOW 2.6.2.1 Discusses refrigerant recycling. Would 100# recovery bottles be acceptable? | SOW states 30# bottles; these requirements need to be followed for bidding.
75 | Are fire alarm as built drawings available? | All available facility asbuilts are provided with these RFI responses. To be clear all existing fire alarm devices and equipment not connect to the existing fire alarm system are to be upgraded to meet current code requirements.
76 | The existing system appears to be a fire alarm system, and not mass notification. Confirm if the intent is a one for one replacement of the fire alarm system or if the intent is to bring the system to current code including upgrading to a mass notification system? | the intenet is to replace the system with and EST-4 system which will include all new devices and bringing the building up to current Fire Code Except for the existing foam system and the module and devices for that system. Upgrade to mass notification is not required.
77 | Will the fire alarm system in the hanger be required to be brought up to current UFC 4-211-01 including but not limited to the following: a) Provide a RSFACU for control and release of the foam / water system and a separate FACU for devices and appliances installed throughout the building that are not part of the water / foam releasing system? b) Activate and abort switches with signs and NEMA ratings per UFC 4-211-01– Does the base know if the existing foam valves and system is capable of both abort and activation? c) Blue rotating or flashing beacons no less than 400cd or equivalent 360-degree LED on 120/208 VAC circuits 20-30 feet above floor. d) NEMA 4 rated devices and conduit located in the hanger bay that are subject to spray. e) Non-addressable or linear heat detection in the hanger in place of the existing intelligent devices. | a. The contractor is not to touch the existing foam system or its existing modules. All other code required fire alarm devices shall be replaced as per current Fire Alarm Code. b. Not in scope c. Not in scope d. Upgrade to NEMA3R e. Linear conductor heat dection with end of line resistors at 6'-0" above finished floor shall be used in place of the existing heat detection devices in the hangar.
78 | Will new Flame detectors be required, or can the existing flame detectors be re-used? | all new Fire Alarm Devices will be required per code.
79 | Please confirm that fire alarm wiring is required to be class A (looped, pulling form both ends of the circuit) and in conduit per the design guide. | Class B wiring is required.
80 | The Statement of Work in paragraph 2.9.5.1 states to provide a complete and functional lightning protection system for Building 140, compliant with UFC 3-575-01. Per the AFMAN 32-1065 A5.1.15 “Adhesive Fasteners for down conductors and cross conductors of an integral system are not allowed on Air Force Facilities due to the short life of the adhesive”. Per the UFC 3-575-01 3-2.1 for Air Force “If adhesive fasteners must be used, an inspector who is familiar with the installation of these adhesive fasteners must watch during the installation and verify in writing (print name after signature) in the test records for that facility / structure that the installation was in accordance with manufacturer’s instructions”. Can adhesive be utilized on this reroof project? Installation under the roofing membrane will be a phasing concern considering the roofing contractor is planning on tearing off and replacing sections each day. Additionally, installing conductor with adhesive fastened on top of the membrane will drastically reduce the number of roof penetrations and chances for a potential leak. | Repeat question. See response to #27
81 | The Design Guide in paragraph 8.12.9 states the preferred method of facility grounding is with a ground ring. AFI 32-1065, a ground counterpoise will be required if individual ground rods cannot achieve a grounding resistance test less than 25ohms. Will a ground loop be required? | Repeat question. See response to #28.
82 | If a ground loop is required, does the loop need to be installed 3’-0” to 8’-0” away from the building foundation as required by AFMAN? | Repeat question. See response to #28.
83 | Per the Peterson SFB Design Guide paragraph 8.7.2 states ground rods shall be copper. Are copper -clad ground rods acceptable? Solid copper ground rods are not readily available. | Repeat question. See response to #30.
84 | What is the concrete thickness on the flight line around building 140? | Repeat question. See response to #31.
85 | Will down conductors be allowed to be run exposed on the skin of the building to avoid unwanted penetrations in the roof? | Repeat question. See response to #32.
86 | The current AMAG panel is in room 205. Will the connection to the base wide network need to be moved out of that area? | See response to #17 and SOW sections 2.12.3, 2.12.7. If existing location is within the secure boundary and accommodates the expectations of the listed requirements above, then connection location can remain here.
87 | SOW 2.9.6.1 does not appear to be shown on the drawings. How many are there, where is fixture type FL to be installed, and what circuits feed them? | See amended drawings included with RFI responses
88 | EP-702 fixture types TRP1, TRP2, and I12 are shown in the drawings but are not included in the fixture schedule. Can the fixture schedule be updated to include these types and requirements? | See amended drawings included with RFI responses
89 | EL-102A shows type A fixtures on detail A1 that appear to need either surface mount or drywall trim kits. Please provide direction. | See amended drawings included with RFI responses
90 | EP-101B 26.07 lists Connectrack as the under-carpet raceway. Please advise if this is an or equal. Is an in-carpet system acceptable? | See SOW2.3.6.5 as well. This is "or equal" type system. The government is open to options on this, as long as the product is low-slope (more gradual than 1:20), concealed below the surface of the carpet, and able to accommodate the various power/comm requirements and associated comm separations.
91 | EP-101B 28.01 cannot be deciphered due to map legend overlay. Please provide details. | See amended drawings included with RFI responses
92 | SOW sections 2.10.3 & 2.10.4 state to provide and install 12-strand OM4 backbone cables from 110A to 106E, and 110A to 203 (one each Black & Red). Please clarify below: a. Please confirm if SIPR/RED backbone cables shall be RED jacketed? b. 2.10.3 & 2.10.4 call out OM4, however, 2.10.8.4 calls out 12-strands of OM1 62.5um and 24-strands of OS2 singlemode. Please confirm the correct backbone cable type and strand count? c. Please clarify the desired connector type (ST/SC/LC) for all fiber optic backbone cabling. We suggest using LC type connectors as they are a small form factor connector with higher density capability. Please advise. | a. it is confirmed b. Confirmed C. LC type is confirmed
93 | Please clarify the requirement of contractor provided and installed “UPLINK MODULE” shown in SOW section 2.10.7. Should this be contractor provided, please provide further information on this equipment requirement. | No, not required to be provided.
94 | On drawing sheet E-000, Special Systems Legend, the “typical” Telecommunications triangle (half shaded/half open) states Voice/Data and the number indicates drops. Please confirm that this symbol with an (N) & (1) represents a single Category 6 F/UTP NIPR cable, not (2) cables (1V/1D)? Same question goes for the SIPR locations. Please advise. | Confirmed. The letter designation clarifies the type of network drop at each location.
95 | SOW sections 2.10.3 & 2.10.4 state to provide and install 12-strand OM4 backbone cables from 110A to 106E, and 110A to 203 (one each Black & Red). Please clarify below: a. Please confirm if SIPR/RED backbone cables shall be RED jacketed? b. 2.10.3 & 2.10.4 call out OM4, however, 2.10.8.4 calls out 12-strands of OM1 62.5um and 24-strands of OS2 singlemode. Please confirm the correct backbone cable type and strand count? c. Please clarify the desired connector type (ST/SC/LC) for all fiber optic backbone cabling. We suggest using LC type connectors as they are a small form factor connector with higher density capability. Please advise. | Repeat question. See response to #92.
96 | Please clarify the requirement of contractor provided and installed “UPLINK MODULE” shown in SOW section 2.10.7. Should this be contractor provided, please provide further information on this equipment requirement? | Repeat question. See response to #93.
97 | On drawing sheet E-000, Special Systems Legend, the “typical” Telecommunications triangle (half shaded/half open) states Voice/Data and the number indicates drops. Please confirm that this symbol with an (N) & (1) represents a single Category 6 F/UTP NIPR cable, not (2) cables (1V/1D)? Same question goes for the SIPR locations. Please advise. | Repeat question. See response to #94.
98 | All EC drawings, GENERAL NOTES – COMM., Note C., states to “provide ¾” EMT unless otherwise noted”. Based on the outside cable diameter of a CommScope Category 6 F/UTP and the CommScope conduit fill calculator, the fill ratio will be over the industry standard of 40% for all locations with (4) drops. We suggest changing this General Note to read 1” minimum conduit size. | it is intended that 3/4" conduit be the minimum conduit in the project over all. All conduit for the COMM/DATA is to be 1" minimum.
99 | Drawing sheets EC-101A & EC-101B, Keyed Note 27.05 states to provide “ladder style cable tray 12” wide with 4” rails”. Please confirm that “cable tray” is desired in lieu of the typical and more commonly used “ladder rack” style runway. Example is Chatsworth Products part# 10250-712. Please advise. | Ladder rack style runway is the intent of this keynote.
100 | The Statement of Work in paragraph 2.9.5.1 states to provide a complete and functional lightning protection system for Building 140, compliant with UFC 3-575-01. Per the AFMAN 32-1065 A5.1.15 “Adhesive Fasteners for down conductors and cross conductors of an integral system are not allowed on Air Force Facilities due to the short life of the adhesive”. Per the UFC 3-575-01 3-2.1 for Air Force “If adhesive fasteners must be used, an inspector who is familiar with the installation of these adhesive fasteners must watch during the installation and verify in writing (print name after signature) in the test records for that facility / structure that the installation was in accordance with manufacturer’s instructions”. Can adhesive be utilized on this reroof project. Installation under the roofing membrane will be a phasing concern considering the roofing contractor is planning on tearing off and replacing sections each day. Additionally, installing conductor with adhesive fastened on top of the membrane will drastically reduce the number of roof penetrations and chances for a potential leak. | Repeat question. See response to #27.
101 | The Design Guide in paragraph 8.12.9 states the preferred method of facility grounding is with a ground ring. AFI 32-1065, a ground counterpoise will be required if individual ground rods cannot achieve a grounding resistance test less than 25ohms. Will a ground loop be required? | Repeat question. See response to #28.
102 | If a ground loop is required, does the loop need to be installed 3’-0” to 8’-0” away form the building foundation as required by AFMAN? | Repeat question. See response to #29.
103 | Per the Peterson SFB Design Guide paragraph 8.7.2 states ground rods shall be copper. Solid copper ground rods are not readily available. Are copper-clad ground rods acceptable? | Repeat question. See response to #30.
104 | What is the concrete thickness on the flight-line around building 140? | Repeat question. See response to #31.
105 | Will down conductors be allowed to be run exposed on the skin of the building to avoid unwanted penetrations in the roof? | Repeat question. See response to #32.
106 | Can government provide existing as-builts for contractor to use as demo plans? | All available facility asbuilts are provided along with these RFI responses.
107 | What is the location of Transformer HV1S? | See response to #8.
108 | What is the location of Panel LVHS? What are the circuits and where to we intercept for this panel? | LVHS is intended to be LV1S. See amended drawings.
109 | On the single line diagram Sheet EP-600 there is no new distribution Panels shown between the new 225KVA transformers and the new downstream 225A panel lineups. Please confirm this is correct. | Confirmed it is correct
110 | Will the gov supply a grounding plan of the new 2000 amp switchboard, the new 225 amp transformers, and the 6 LV panels (all part of the new service design). | No grounding plan is required as the grounding conductors are listed on the one-line diagram.
111 | SOW 2.9.1 – Mentions 12470 transformer with a 208 volt service into building, is there any requirements for this service, it to be left in place? If not, what is the size of the service and what should the contractor do with it? | No new requirments for the 208 volt service, existing 120/208V transformer to be removed, see SOW
112 | No re-feeding of any existing mechanical equipment is mentioned. Are there any that require re-feed equipment out of the new panels? | It is intended that all existing electrical p[owered equipment will be powered out of a new electrical panel. Contractor is to evaluate the not in scope areas to determine the number of circuits and the amps required for the breakers in the new panel. All of the new panels are large enough that the existing load can be conneted to any panel as required.
113 | Lighting plans do not show any em lights, switching, or controls. Can the government please provide? | See amended drawings included with RFI responses
114 | Are existing lamps and ballast to be turned over to PSFB? | Existing lamps and ballasts are to be disposed of by the contractor.
115 | Is it a requirement to keep existing roof-top rotating beacons powered during construction efforts. Where is the feed for these lights located? How big is this feed? | There are existing obstruction lights on roof that will need to be reinstalled, yet maintained operational throughout construction. See SOW.
116 | Sow 9.6.2024 Gen Req: 2.9.2 Remove all existing light fixtures, light switches, receptacles, conduit, conductors, boxes, buss duct and all electrical equipment in the scope of work area. All conduit and conductors are to be removed back to source if they don’t interfere with an “out of scope area”. All other electrical light fixtures, switches, receptacles, conduits, conductors, etc. that are in “out of scope” spaces are to remain as is. If the electrical circuit that is in the “out of scope” area is supplied by a circuit that is adjacent to the space leave the conductors conduit and all electrical devices in the “out of scope” area are to remain. A new circuit will be supplied to the space via a new home run from a new electrical panel. | There is no question here. Yes, this is what the SOW says.
117 | Will some of the building areas be occupied during the construction? | Yes, contractor can assume all areas outside the "Scope Areas" on Sheet G002 will have occupants throughout construction. Primarily, the routinely occupied area is the CAP suite in Area A 1st floor and the main Hangar bay. Other areas will receive occasional occupants/visitors.
118 | Is the fire alarm in the hanger/bay and in NIC areas to be brought up to code or remain as is? | See response above.
119 | Sow 2.9.2.2. Remove all the existing electrical panels located in the hanger on the north and south walls. All existing conduits and conductors are to remain in the same location of the removed electrical panels for possible re-use if they service the hanger area. The (2) two existing conduits 4-inch conduits that feed from the north duct to the south duct along the ceiling are to remain. If there are any circuits feeding an “out of scope area” they are to be fed temporarily from another electrical panel. This panel can be used to supply temporary power to those areas with personnel. The areas that are not in scope will be tied into a new electrical panel in the hanger area. A new electrical panel will be placed on the hanger wall on the north and on the south walls. Question: can government suggest a qty of new circuits, types of conduit and wire sizes with distance contractors are to propose on? | See electrical drawings
120 | 2.9.3.1. Provide and install a new (MSB) 2000A, 480/277V, 3 Phase, NEMA3R rated switchboard, size all breakers as shown in the drawings. Provide and install (2) new 480/277V – 208/120V three phase, NEMA3R dry type transformers. Provide and install (2) new 480/277V, 3 phase electrical panels (1) 1000A and (1) 600A rated, AIC rating and panel information is shown in the drawings. Provide (6) 208/120V, 225A, 84 circuit, 3 phase, electrical panels, AIC ratings and panel information is shown in the drawings. This shall include all conduit, conductors, conduit support brackets, breakers, and electrical fittings required for a complete and functional system as shown on the drawings. All new switchboards, and panels are to have external power meters, see design guide for power meter. Question: per the design guide, new services are to have a meter on the incoming switchgear. Are the downstream panels also required to have a meter per the statement above? | Yes, all down stream panels are to have external power demand meters as well.
121 | Will the base drain the water to keep pipes from freezing? | No, the contractor is responsible for ensuring freeze protection as listed above.
122 | Can you provide mechanical as builds/demo plans? | All available facility asbuilts are provided with these RFI responses.
123 | Who is the preferred Control Contractor? | There is no preferred controls contractor; the basewide system in Johnson Controls. Any contractors working on the system just must be certified to work on Johnson Controls Metasys systemsand fluent in the JCI system.
124 | Will this work be going in phases? | There are specific requirements outlined within the SOW (1.12) that will require attention for sequencing. Aside from the provisions outlined within the SOW and Drawings, phasing/sequencing is a means and methods provision of this project.
125 | Is temporary heating and cooling needed? | See previous responses.
126 | SOW 2.9.2 are there going to be electrical demolition drawings released? | no. Existing facility abuilts are being provided with RFI responses. Additionally, two contractor site walks have occurred for in-field conditions.
127 | SOW 2.9.2.2 Is there a reason why the (2) 4” conduits for the bus duct are to remain, When the bus ducts are being demolished? | Yes, they can be used to supply power to HVS1 panel.
128 | SOW 2.9.2.2 Is there an estimated electrical load that is going to be needed to be furnished for existing out of scope power requirements during construction for temporary power. | This is method and means. The contractor can choose to leave the existing circuits powered until the new panels are installed or the contractor is to provide temporary power for all out of scope areas. Either way it will require the contractor to analyze the existing electrical in those areas.
129 | SOW 2.9.2.2 what is the plan for out-of-scope permanent power. This section states these loads will be tied into new panel provided on hangar wall but panel schedule on drawing E701 Panel LVHN has no loads connected to it. | the existing circuits and number of circuits are to be inspected by the electrical contractor prior to connecting the circuit to the new electrical panels.
130 | SOW 2.9.3 Please clarify the locations of the (2) 480V-208V Nema 3R dry type transformers. ( they will be noted as Transformer HV1N and Transformer HV1S in these questions per the panel schedules). a. Transformer HV1N appears to be in room 112A on drawing EP-101B. cannot locate HV1S on drawings, there is a HV1 transformer on drawing EP-101A located outside by chiller CH-1 is this the correct placement of transformer HV1S? please see attachment b. With the current location of Panel LV2N will there need to be a circuit breaker enclosure on the secondary side of the transformer due to not meeting the conditions of NEC code 240.21 for the tap rule. c. If that is the correct placement of transformer HV1S, will there need to be a circuit breaker enclosure on the secondary side of the transformer due to not meeting the conditions of NEC Code 240.21 for the 10/25 tap rule. | a. Yes b. Correct c. Correct
131 | Please confirm that the New MSB will be in Rm 112A where the existing switchboard is currently located. There are concerns about clearances in room 112A for the addition of New 2000A MSB. | No, room 112
132 | Which is the preferred method for installing the new (6) 4” feeder conduits from the existing transformer to the new MSB due to existing location and site conditions. Are the secondary feeders to be concrete encased? | This is methods and means. Run the conduit from the existing utility transformer to the new MSB in room 112. The secondary conductors are not to be encased in concrete. Do not cut the existing concrete.
133 | Please clarify the location of Panel LVHS and what drawing sheet it is located on. | LVHS is LV1S. See revised drawings
134 | Will the hangar be fully operational during construction? Will there be any area inside the hangar for storage. | See SOW 1.18
135 | Will there be a laydown for storage connex placement and where will it be located. | See SOW 1.13 and 1.14. Purpose of free zone is to permit Contractor to define the most effective site management methodology.
136 | Roof drawing 1/A-103 offers no detail cuts for flashings. Can the owner provide latest “AS-BUILT” set of structural & Architectural drawings to bidders ? ( including roof details, elevations and wall cuts ) | All existing facility asbuilts have been provided with these RFI responses.
137 | UFC 3-110-03 of 09-26-2006 has specific requirements for deck slopes. Supplied plans do not offer the structural deck slopes or areas of construction requiring full tapered insulations. ( As-builts may contain the data needed to put this proposal together ) | All existing facility asbuilts have been provided with these RFI responses. Purpose of contractor site walk (Conducted 18 SEP) is to fill any remaining gaps to complement existing facility information.
138 | See page 29, para. 5-2.2.2- Slope: “ Every effort must be made to achieve 1/2:12. Are existing slopes ½:12 in the structure or achieved with tapered insulations ? | See response to #163
139 | Please verify length of warranty desired; Wind uplift rating desired; hail size coverage desired;. | Review SOW 2.14.3
140 | Please verify R-value of insulation desired. | R-value 49 attic insulation for SSMR, R-value 30 continuous insulation for mod bit (Review SOW 2.14.23.2)
141 | Please verify if a vapor barrier is desired. | SOW section 2.14.23.1.22 requires the Contractor to provide a transient hygrothermal analysis indicating a satisfactory vapor control solution for this project. The need for a vapor retarder as part of the roofing assembly will be determined by the combination of this analysis tied directly to the specific assembly materials proposed/submitted by the awarded team (Combination of R-values, perm values, and surface color characteristics)
142 | What is gauge and type of metal is preferred for roofing details ? Metal Roofing? | 22 gage minimum, steel roof material is preferred.
143 | At the metal roof areas: will the existing roof sheathing remain? What is the panel width desired: What is seam height desired ? | Contractor is to assume that 10% of roof decking shall be replaced (SOW 2.14.6). Panel width desired is 16". Seam height desired is 2" minimum
144 | Is “white” gravel desired on the low-slope roof areas ? | See PSFB Design Guide 5.6.10.2 and SOW 2.14.23.1.22
145 | Since there are no roof details in this package, are there any assumptions that additional wood blocking may be needed? | Existing facility asbuilts have been provided with these RFI responses. Additionally, see SOW sections 2.14.15, 2.14.17, and 2.14.23.2.12.
146 | SOW sections 2.10.3 & 2.10.4 state to provide and install 12-strand OM4 backbone cables from 110A to 106E, and 110A to 203 (one each Black & Red). Please clarify: Please confirm if SIPR/RED backbone cables shall be RED jacketed? | See response above
147 | SOW 2.10.3 & 2.10.4 call out OM4, however, 2.10.8.4 calls out 12-strands of OM1 62.5um and 24-strands of OS2 singlemode. Please confirm the correct backbone cable type and strand count? | See response above
148 | Please clarify the desired connector type (ST/SC/LC) for all fiber optic backbone cabling. We suggest using LC type connectors as they are a small form factor connector with higher density capability. Please advise. | See response above
149 | Please clarify the requirement of contractor provided and installed “UPLINK MODULE” shown in SOW section 2.10.7. Should this be contractor provided? Please provide further information on this equipment requirement. | See response above
150 | On drawing sheet E-000, Special Systems Legend, the “typical” Telecommunications triangle (half shaded/half open) states Voice/Data and the number indicates drops. Please confirm that this symbol with an (N) & (1) represents a single Category 6 F/UTP NIPR cable, not (2) cables (1V/1D)? Same question goes for the SIPR locations. Please advise. | See response above
151 | All EC drawings, GENERAL NOTES – COMM., Note C., states to “provide ¾” EMT unless otherwise noted”. Based on the outside cable diameter of a CommScope Category 6 F/UTP and the CommScope conduit fill calculator, the fill ratio will be over the industry standard of 40% for all locations with (4) drops. We suggest changing this General Note to read 1” minimum conduit size. | See response above
152 | Drawing sheets EC-101A & EC-101B, Keyed Note 27.05 states to provide “ladder style cable tray 12” wide with 4” rails”. Please confirm that “cable tray” is desired in lieu of the typical and more commonly used “ladder rack” style runway. | See response above
153 | There appear to be no plumbing or Mechanical demo drawings? Can plumbing and mechanical demo drawings be provided? | See SOW and G002 for demolition requirements.
154 | Mechanical drawings do not show 3" chilled water supply and return going from Area A to Area B? Can the Government Confirm 3" chilled water supply and return will need to run from Area A to Area B through the hangar bay approximately 100' in distance and 30'-40' in elevation? Can new drawings reflect this? | Yes the chilled water line is intended to run along a similar path to the existing hot water line as is shown in the drawings. A drawing showing this could be created if its really needed as it's modeled but the line will not show well at the scale of the whole building. A competant piping contractor should be able to "connect the dots" on this. - let me know if you want a sheet
155 | Condensate piping is not shown on the drawings from all the fan coil units? Can condensate pipe sizing and routing be shown on drawings or is it for the plumbing contractor to design and route? | Plumbing contractor should be able to route; condensate piping is typically not shown but shop drawings could be provided for concurrence if desired.
156 | Can the government confirm the existing heating water piping system can be reused? | Yes see SOW requirements.
157 | Can the government confirm existing Heating Water Boilers, Pumps, Expansion tank will be reused and not modified? | Yes existing equipment is planned to remain for the hot water plant.
158 | Does current heating water system have glycol? If so, can the gov't confirm Heating water system will require a complete flush and new glycol? | Yes it should be 35% P.G. as listed in the drawings.
159 | Existing Water heaters appear to be electric. Drawing appears to show a gas water heater but there is no fixture schedule for the water heater? Is the new water heater to be gas or electric? If Gas can gas piping routing be shown on drawings? | Existing domestic water heater is electric and should be demolished. New WH-1 is to be gas-fired as shown. WH-2 is existing and shows to remain.
160 | Plumbing drawings do not show pipe sizing for new piping. Can pipe size be shown for new plumbing piping? | Pipe sizes follow standard IPC rules, but can be shown in drawings.
161 | SOW Section 2.6.3.5 states the chiller has to be the same manufacture as the AHUs? Our understanding is that there is an existing sole source letter in place for Trane chillers correct? So intent is that Can AHUs and FCUs must be Trane as well? | Yes the SOW limits the Chiller and AHU to the same manufacturer. Yes there is a sole source to Trane for all Chilers. Unclear what the last question is asking. However FCU's and AHU's are not required to be the same manufacturer.
162 | Will there be any work performed on the metal vertical siding on this complex, or will the only metal roofing addressed be “sloped” metal roofing areas ? | Yes, there will be select work on vertical metal panels due to electrical and mechanical penetrations, door opening enlargement, etc. However, it is expected that this work is primarly selective demolition and metal trim work to re-finish new openings, not to provide new full paneling for any vertical wall on the facility. Unsure if this question is in relation to the standing seam metal roofing, but wall paneling is not standing seam.
163 | Will any of the low-slope decks require “full” tapered insulation assemblies ? | All available existing facility asbuilts have been provided with these RFI responses. Full tapered insulation is expected on any roofs that have flat structural slope to achieve the proper minimum net slope outlined in the SOW. However, SOW section 2.14.23.2 allows for reduced slope to match existing roof slope where steeper slope is not feasible due to exterior cladding height limitations or other conflicts. The Government expects flat structure exists along the full extent of the first floor roof, canopy roof, and lower 2nd floor roof all on the flight line side. See revised SOW section 2.14.23.2 for more information.
164 | Is there any asbestos in the existing low-slope roof areas | No asbestos is expected however contractor shall provide their own asbestos and hazardous material testing (Review SOW 2.2)